# Industrial NTP Time Server — Bid Technical Proposal

| Item | Content |
| --- | --- |
| Audience | Agents / end customers / tender package |
| Document title | Bid Technical Proposal |
| Doc No. | `DOC-Q3000-BID-EN-011` |
| Product model | QYTS-3000-BG-T-S |
| Document type | Bid / tender technical proposal (project name fillable) |
| Document version | 1.0 |
| Firmware baseline | V4.9.0 (see nameplate / Web “Firmware / Build”) |
| Companion attachments | Product Specification (Shipping); Reference · Serve Policy · Capacity (One Page); User Guide (bid-sanitized); Industrial Interface Protocol |

Fill before submission:

Tender / project name: ____________________

Tender No.: ____________________

Bidder: ____________________

Date: ____________________

# 1. Purpose and Basis

## 1.1 Purpose

This document responds to tender requirements for a LAN time server / GNSS-synchronized clock / NTP stratum-1 appliance, covering architecture, performance claims, interfaces, deployment, and acceptance recommendations for technical evaluation.

## 1.2 Basis

Purchaser’s tender documents (controlling text)

Shipping Product Specification Product Specification (Shipping)

One-pager Reference · Serve Policy · Capacity Selection Sheet (Reference · Policy · Capacity)

Bid-sanitized User Guide 用户指南（标书脱敏版） (do not attach the shipping edition that contains factory credentials)

Industrial Interface Protocol 工业接口协议附件

NTP RFC 5905 (server-side common subset as implemented)

Modbus RTU industrial practice (9600 8N1 slave)

## 1.3 Response Principles

Per-channel claims: NTP, RS-485 Modbus, TTL 1PPS, and IRIG-B120 metrics are independent and must not be cross-applied.

Testable: Contracted metrics should map to practical acceptance methods (Section 6).

Clear exclusions: Capabilities not implemented (PTP/IEEE 1588, dual-port redundancy, IPv6, NTS, etc.) are not claimed.

# 2. Understanding and Overall Solution

## 2.1 Typical Needs

| Consumer | Typical need | Channel |
| --- | --- | --- |
| Servers / PCs / NVR / switches | LAN NTP | RJ45 NTP |
| PLC / SCADA / HMI | Absolute time stamps | RS-485 Modbus |
| DAQ / scopes / sync nodes | Hardware second edge | TTL 1PPS |
| Power / legacy timing gear | IRIG-B | IRIG-B120 DCLS |

## 2.2 Technical Approach

GNSS 1PPS + local oscillator disciplining + RTC/SQW holdover + parallel multi-channel outputs:

Outdoor GNSS antenna
        │
        ▼
 GNSS module (1PPS + navigation data)
        │
        ▼
 Disciplining / phase monitor / state machine (LOCK / HOLDOVER)
        ├──► RJ45: NTP server + Web management
        ├──► RS-485: Modbus RTU absolute time
        ├──► TTL: 1PPS
        └──► IRIG-B120: DCLS timecode

After LOCK, the unit operates as an NTP Stratum 1 server. Brief GNSS loss enters Holdover with degrading quality over time (see Product Spec).

## 2.3 Evaluation Highlights

| Point | Description |
| --- | --- |
| Primary reference | GNSS-based; not dependent on an upstream NTP server |
| IT + OT in one box | NTP plus Modbus / PPS / IRIG |
| Operability | Web Dashboard, LCD, event & 24h quality CSV export |
| Traceability | Factory SETID; firmware Build ID |
| Compliant wording | Accuracy stated per interface — no “10 ns over Ethernet” claim |

# 3. Scope of Supply

## 3.1 Hardware

| No. | Item | Notes |
| --- | --- | --- |
| 1 | QYTS-3000-BG-T-S time server | Ethernet, RS-485, 1PPS, IRIG (this SKU) |
| 2 | GNSS antenna & cable (per contract) | Outdoor, clear sky view |
| 3 | Power (single path `-S`, per contract / nameplate) | One inlet at a time: (1) AC 220 V IEC 3-pin (onboard AC module); or (2) DC-IN (DC050-T) + external adapter (12–24 V DC). Never both; not dual-redundant `-D` |
| 4 | Shipping documents | User guide, spec, protocol, wiring pack |

Cabinet, switches, client software, and PLC engineering are by others unless contracted.

## 3.2 Firmware / Software

Factory firmware (version per nameplate / Web)

Built-in HTTP UI (Basic Auth)

NTP at boot; Modbus / 1PPS / IRIG per SKU

# 4. Key Technical Responses

## 4.1 Basics

| Common tender item | Response |
| --- | --- |
| Product class | GNSS-disciplined LAN NTP time server |
| Model | QYTS-3000-BG-T-S |
| Constellation / Osc / Power | BG (BeiDou+GPS) / T (TCXO) / S (single supply) |
| Protocol | NTP v3/v4, UDP 123 |
| Network | 1× RJ45, 10/100M (single port; not dual-port HA) |
| Default IP | 192.168.1.123/24, gw 192.168.1.1 (configurable) |
| Management | Web + front LCD |
| Time reference | GNSS 1PPS + TCXO discipline; industrial RTC (temp-compensated) / SQW holdover |

## 4.2 Accuracy (Per Channel, after LOCK)

| Channel | Typical claim | Acceptance |
| --- | --- | --- |
| Internal / GNSS 1PPS reference | Module short-term stability typically ≤ 10 ns RMS; internal jitter monitor typically ≤ 50 ns (short window) | Lab / factory |
| TTL 1PPS out | Sub-µs edge vs internal PPS | Scope / TIC |
| RS-485 Modbus | 1 ms resolution (UTC incl. ms) | PLC register compare |
| Ethernet NTP | Typical LAN millisecond class (measure at client) | ntpq / chronyc / client logs |
| Holdover | Continues after brief GNSS loss; error grows with time | Antenna-pull soak |

Contract note: Internal “10 ns RMS” must not be equated to “10 ns NTP at the client” or “nanosecond Modbus.” Specify acceptance per interface.

## 4.3 NTP Capacity

| Item | Response |
| --- | --- |
| Role | NTP server; typically Stratum 1 after LOCK |
| Recommended clients | ≤ 60 on LAN |
| Global replies | Adaptive rate limit; overload protect ≈ ≤ 1024/s |
| Per-source IP | ≤ 8/s |
| ACL | Optional NTP source whitelist |
| Warm-up policy | Optional Stratum-2 transitional replies via Web policy (factory default: reply when locked) |

## 4.4 Industrial Interfaces

| Interface | Response |
| --- | --- |
| RS-485 | Modbus RTU slave, 9600 8N1, ID 0x01; FC 0x03/0x04; UTC with ms |
| 1PPS OUT | TTL second pulse |
| IRIG-B120 | DCLS, aligned to PPS second (this SKU) |

Register map and bring-up: Industrial Interface Protocol.

## 4.5 Management & Logs

| Item | Response |
| --- | --- |
| Web | Dashboard / Network; HTTP Basic Auth |
| SNMP | Read-only SNMPv2c / UDP 161 (b140+); no HTTPS / SNMPv3 |
| Event log | `event_log.csv` (~2048-entry ring; default export ~latest 1024); Dashboard → Diagnostics → Export |
| 24h quality | `quality_24h.csv`; hourly rows; `samples=0` = no GNSS-disciplined samples that hour |
| LCD | Inspection / decision / diagnosis / asset pages |

## 4.6 Explicit Exclusions

Not in standard scope (unless a separate solution is bid):

PTP / IEEE 1588 and plant-wide sub-µs Ethernet timing

NTS, IPv6, NTP broadcast/multicast server

Dual Ethernet redundancy / failover

Nanosecond fieldbus timing

HTTPS, SNMPv3, SNMP write (on-device SNMP is v2c read-only only)

# 5. Integration Outline

## 5.1 IT (Network)

Connect to LAN (prefer management VLAN).

Set static IP; ensure UDP 123 reachability.

Point clients to device IP (`iburst` recommended).

Optional NTP source whitelist.

## 5.2 OT (Industrial)

RS-485 wiring per practice (120 Ω termination, common ground).

PLC/SCADA poll calendar registers (suggest ≥ 1 Hz) via FC03.

Edge sync → TTL 1PPS; legacy timecode → IRIG-B120.

## 5.3 Antenna

Outdoor clear sky; quality feedline; treat LOCK as prerequisite for official timing use.

## 5.4 Responsibility Split

| Party | Scope |
| --- | --- |
| Bidder (supply) | Device, factory config, docs, training (per contract) |
| Integrator | Rack power, network design, PLC, bulk client config |
| End user | Patrol, antenna care, accounts / ACL |

# 6. Suggested Acceptance

## 6.1 Incoming

Model, SETID, firmware Build vs packing list; power-on Web/LCD; SN visible.

## 6.2 Functional (suggested)

| No. | Item | Method | Pass (suggested) |
| --- | --- | --- | --- |
| 1 | GNSS lock | Antenna OK; LCD/Web | LOCK / Stratum 1 |
| 2 | NTP | Same-subnet client | Stable ms-class offset (site network dependent) |
| 3 | Modbus | Master reads Y/M/D h:m:s.ms | Matches reference within 1 ms resolution |
| 4 | 1PPS | Oscilloscope | Stable second pulse |
| 5 | IRIG | Receiver or scope | Frame OK (if in contract) |
| 6 | Logs | Download event_log / quality_24h from Dashboard Diagnostics | Readable; quality includes hourly rows (incl. samples=0) |

## 6.3 Accuracy Wording

Contract must name the acceptance interface. Do not apply internal 10 ns figures to NTP client tests.

# 7. Reliability & Operations

State machine visible on LCD/Web; Ethernet soft recovery paths and external-watchdog power-cycle strategy for hard faults (firmware policy); CSV logs for support; Web-configurable IP / NTP policy / ACL (see User Guide).

# 8. Implementation Schedule (Template)

| Phase | Work | Suggested duration |
| --- | --- | --- |
| T0 | Kickoff, IP/antenna plan | 3–5 working days |
| T1 | Delivery & incoming inspection | Per contract |
| T2 | Install, power, cabling | 1–2 days / site |
| T3 | Integration (NTP / PLC / timecode) | 1–3 days / site |
| T4 | Training & handover | 0.5–1 day |
| T5 | Trial run & final acceptance | Per tender |

# 9. Training & Warranty (Template)

Training: install notes, Web/LCD patrol, NTP & Modbus bring-up, log export + SETID/Build for support tickets.

| Item | Fill per commercial terms |
| --- | --- |
| Warranty | ____ years |
| Support | Phone / remote / on-site |
| Spares | ________________ |

# 10. Clause-by-Clause Response Matrix (Template)

| No. | Tender clause (summary) | Bid response | Status | Evidence |
| --- | --- | --- | --- | --- |
| 1 | NTP server | UDP 123; Stratum 1 after LOCK | Full | Spec §5 |
| 2 | GNSS timing | GNSS 1PPS discipline | Full | Spec §1 |
| 3 | Web management | HTTP Basic Auth | Full | User Guide |
| 4 | RS-485 absolute time | Modbus RTU, 1 ms | Full | Protocol annex |
| 5 | 1PPS output | TTL 1PPS | Full | Spec §7 |
| 6 | IRIG-B | IRIG-B120 DCLS (this SKU) | Full | Protocol annex |
| 7 | Dual-port redundancy | Single port | Deviation / N/A | §4.6 |
| 8 | PTP/1588 | Not included | Deviation / N/A | §4.6 |
| 9 | … | … | … | … |

# 11. Deviation Statement (If Required)

For each deviation: clause ID, actual capability, mitigation/impact, and whether it is material (legal/commercial review).

Common proactive statement: This product is a single-port industrial NTP appliance and is not bid as a PTP plant-wide sub-µs solution. If PTP is mandatory, use a dedicated PTP design or consortium bid.

# 12. Attachment List

| No. | Attachment | Format | Notes |
| --- | --- | --- | --- |
| A1 | Product Specification (Shipping) ZH | md/docx | Product Specification (Shipping, ZH) |
| A2 | Product Specification (Shipping) EN | md/docx | Product Specification (Shipping) |
| A3 | Reference · Serve Policy · Capacity (One Page) | md/docx | Selection Sheet (Reference · Policy · Capacity) |
| A4 | User Guide (bid-sanitized) | md/docx | 用户指南（标书脱敏版） (not the shipping edition with factory password) |
| A5 | Industrial Interface Protocol | md | 工业接口协议附件 |
| A6 | This Bid Technical Proposal | md/docx | Bid Technical Proposal |
| A6 | Datasheet / photos | optional | Commercial pack |
| A7 | Test / factory reports | optional | Per contract |

Packaging: Tender ZIP must contain only files from this public technical package. Do not include the shipping User Guide (factory credentials), internal unpublished technical materials.

# 13. Closing

QYTS-3000-BG-T-S addresses common industrial, security, office, and metering-assist needs for a local GNSS authority with multi-channel timing. The bidder affirms consistency with the shipping specification and protocol annex; acceptance is per channel; exclusions in §4.6 are not falsely claimed.

Commercial terms (price, delivery, warranty) are governed by the commercial bid volume.