# Industrial NTP Time Server — Product Specification (Shipping)

| Item | Content |
| --- | --- |
| Audience | Agents / end customers / tender package |
| Document title | Product Specification (Shipping) |
| Doc No. | `DOC-Q3000-DS-EN-011` |
| Model | QYTS-3000-BG-T-S |
| Document version | 1.1 |
| Firmware | V4.9.0 (see device label / Web Dashboard Firmware & Build) |
| Related documents | User Guide (bid-sanitized); Industrial Interface Protocol (annex) |
| One-pager | Selection Sheet (Reference · Policy · Capacity) |

# 1. Overview

GNSS-disciplined LAN NTP Stratum 1 time server providing Ethernet NTP, RS-485 Modbus absolute time, TTL 1PPS output, and IRIG-B120 (this SKU). For industrial, security, office, and auxiliary metrology timing.

| Item | Specification |
| --- | --- |
| Commercial model | QYTS-3000-BG-T-S |
| Constellation code | BG = BeiDou + GPS (UI may show `BD+GPS`) |
| Oscillator / Power | T = TCXO; S = single supply |
| Timing protocol | NTP v3/v4 (UDP 123) |
| Time reference | GNSS 1PPS + TCXO discipline; industrial RTC (temp-compensated) / SQW holdover |
| Management | Web (HTTP Basic Auth) + front-panel LCD; SNMP read-only (UDP 161, SNMPv2c) |
| Identity | Factory SETID (Web / LCD: `SN:`) |

# 2. Electrical & Environment (summary)

| Item | Specification |
| --- | --- |
| Power | Single path `-S`. Two inlets; use only one at a time: (1) AC 220 V IEC 3-pin inlet (onboard isolated step-down + filter/rectifier, ≈12.5 V internal rail); (2) DC-IN (DC050-T) + external adapter, 12–24 V DC (see nameplate/adapter). Do not feed AC and DC together. Export: plug/adapter per order. Not dual-redundant (`-D`) |
| Ethernet | 1× RJ45, 10/100M (single port; not dual-port redundancy) |
| Operating temperature | Per hardware datasheet / nameplate |
| Default IP | 192.168.1.123 / 255.255.255.0 / gateway 192.168.1.1 |

# 3. Interfaces

| Interface | Function | Notes |
| --- | --- | --- |
| RJ45 | NTP + Web | Same IP/MAC; not a second independent port |
| RS-485 | Modbus RTU slave | Absolute UTC time registers (incl. ms) |
| 1PPS OUT | TTL pulse-per-second | Hardware second edge |
| IRIG-B120 | DCLS timecode | Frame output aligned to PPS |
| GNSS antenna | Fix + 1PPS | Outdoor antenna as installed |
| Front panel | LCD + single key | Ops / status display |

# 4. Timing Accuracy (by channel)

Metrics of different interfaces must not be mixed.

| Channel | Typical capability (after LOCK) | Use |
| --- | --- | --- |
| Internal / GNSS 1PPS reference | Module short-term ≤ 10 ns RMS; internal jitter monitor ≤ 50 ns (short window) | Factory / acceptance reference |
| TTL 1PPS OUT | Sub-microsecond edge (vs internal PPS) | Hardware second-edge sync |
| RS-485 Modbus | 1 ms resolution | PLC / SCADA absolute time |
| Ethernet NTP | Typical millisecond class on LAN (verify on client) | PCs / servers / switches |
| Holdover | Degrades toward ppm with unlock time | Short GNSS outages |

Important: “GNSS 1PPS 10 ns RMS” is not “NTP client 10 ns” or “nanosecond Modbus timing.”

# 5. NTP Service

| Item | Specification |
| --- | --- |
| Mode | NTP server (RFC 5905 subset) |
| After LOCK | Typically Stratum 1 |
| Warm-up / policy window | May reply Stratum 2 per Web serve policy (factory default: lock-based serve) |
| Recommended clients | ≤ 60 on LAN |
| Global replies | Adaptive rate limit (no low hard cap under normal load); overload protect ≈ ≤ 1024/s; further derated during large Web exports |
| Per source IP | ≤ 8 replies/s |
| ACL | Optional NTP source IP allow-list (Web) |

Not included: PTP/IEEE 1588 stack, NTS, dual-port failover, IPv6, NTP broadcast/multicast server, HTTPS, SNMPv3 / SNMP write.

# 6. RS-485 Modbus RTU

| Item | Specification |
| --- | --- |
| Link | 9600 8N1 |
| Slave ID | 0x01 |
| Function codes | Read 0x03 / 0x04 (write only for factory use; see protocol annex) |
| Clock registers | UTC Y/M/D/h/m/s/ms |
| Poll rate | Recommend ≥ 1 Hz |

Full register map: Industrial Interface Protocol annex.

# 7. 1PPS & IRIG (summary)

| Item | 1PPS OUT | IRIG-B120 |
| --- | --- | --- |
| Level | 3.3 V TTL (per terminal/datasheet) | Per hardware datasheet |
| Role | Second-edge sync | Legacy timecode |
| Absolute time | Pulse = second boundary; calendar via Modbus/NTP | Same |

# 8. Management & Logs

| Item | Specification |
| --- | --- |
| Web | Dashboard / Network; Basic Auth |
| SNMP | Read-only SNMPv2c, UDP 161; MIB-II system + device status; no Set / SNMPv3 / Trap; enterprise PEN provisional |
| Syslog | Optional UDP edge push (default OFF); same dictionary as `event_log`; Web Network configures target IP:514 |
| Event log | `event_log.csv` (`/flog`), ring ~2048 entries; default export ~latest 1024; Dashboard → Diagnostics → Export |
| 24 h quality | `quality_24h.csv` (`/stats24`); hourly buckets; `samples=0` = no GNSS-disciplined samples that hour |
| Front panel | Four pages: patrol / decide / diagnose / asset |

# 9. Ordering & Traceability

Record on the shipping sheet:

Model: QYTS-3000-BG-T-S
SETID: _______________
FW_BUILD_ID: _______________
Production test: PASS / FAIL

# 10. Related Documents

| Document | Content |
| --- | --- |
| Reference · Serve Policy · Capacity (One Page) | Selection Sheet (Reference · Policy · Capacity) |
| User Guide | Power-up, LCD, Web, clients, FAQ |
| Industrial Interface Protocol | Modbus map, IRIG, integration checklist |
| This specification | Contract / selection boundaries |

This document is a shipping/contract summary. Implementation details follow the annex and the shipped firmware.