# Industrial NTP Time Server — Product Specification (Shipping)

| Item | Content |
| --- | --- |
| Audience | Agents / end customers / tender package |
| Document title | Product Specification (Shipping) |
| Doc No. | DOC-TS3000-DS-EN-011 |
| Model | TempoSync-3000-BG-T-S |
| Document version | 1.3 (this respin: hardware 1PPS, no IRIG, Pin4 minute pulse; no OCXO) |
| Firmware | V4.9.0 (see device label / Web Dashboard Firmware & Build) |
| Related documents | User Guide (bid-sanitized); Industrial Interface Protocol (annex) |
| One-pager | Selection Sheet (Reference · Policy · Capacity) |

## 1. Overview

GNSS-disciplined LAN NTP Stratum 1 time server providing Ethernet NTP, RS-485 Modbus absolute time, TTL 1PPS (GNSS edge via 硬件缓冲), and a four-pin PPM pulse. For industrial, security, office, and auxiliary metrology timing. This respin has no IRIG.

| Item | Specification |
| --- | --- |
| Commercial model | TempoSync-3000-BG-T-S |
| Constellation code | BG = BeiDou + GPS (UI may show BD+GPS) |
| Oscillator / Power | T = TCXO; S = single supply |
| Timing protocol | NTP v3/v4 (UDP 123) |
| Time reference | GNSS 1PPS + TCXO discipline; industrial RTC holdover (temperature-compensated) |
| Management | Web (HTTP Basic Auth) + front-panel LCD; SNMP read-only (UDP 161, SNMPv2c) |
| Identity | Factory SETID (Web / LCD: SN:) |

## 2. Electrical & Environment (summary)

| Item | Specification |
| --- | --- |
| Power | Single path -S. Two inlets; use only one at a time: (1) AC 220 V IEC-style inlet (isolated step-down); (2) DC-IN + external adapter, 12–24 V DC (see nameplate/adapter). Do not feed AC and DC together. Export: plug/adapter per order. Not dual-redundant (-D) |
| Ethernet | 1× RJ45, 10/100M (single port; not dual-port redundancy) |
| Operating temperature | Per hardware datasheet / nameplate |
| Default IP | 192.168.1.123 / 255.255.255.0 / gateway 192.168.1.1 |

## 3. Interfaces

| Interface | Function | Notes |
| --- | --- | --- |
| RJ45 | NTP + Web | Same IP/MAC; not a second independent port |
| RS-485 | Modbus RTU slave | Absolute UTC time registers (incl. ms) |
| 1PPS OUT | TTL pulse-per-second | 硬件缓冲 GNSS-edge fan-out (3.3 V); not MCU-driven |
| PULSE | PPM | 4-pin Pin4; 200 ms at UTC minute after LOCK (5 V via level shifter) |
| GNSS antenna | Fix + 1PPS | Outdoor antenna as installed |
| Front panel | LCD + single key | Ops / status display |

## 4. Timing Accuracy (by channel)

Metrics of different interfaces must not be mixed.

| Channel | Typical capability (after LOCK) | Use |
| --- | --- | --- |
| Internal / GNSS 1PPS reference | Short-term typically ≤ 10 ns RMS (see validation report) | Factory / acceptance reference |
| TTL 1PPS OUT | GNSS second edge via hardware buffer | Hardware second-edge sync |
| RS-485 Modbus | 1 ms resolution | PLC / SCADA absolute time |
| Ethernet NTP | Lab clause: LOCK + low LAN RTT → client offset can reach ms class (see report); no arbitrary-field guarantee | PCs / servers / switches |
| Holdover | Degrades toward ppm with unlock time | Short GNSS outages |

Important: “GNSS 1PPS 10 ns RMS” is not “NTP client 10 ns” or “nanosecond Modbus timing.”

## 5. NTP Service

| Item | Specification |
| --- | --- |
| Mode | NTP server (RFC 5905 subset) |
| After LOCK | Typically Stratum 1 |
| Warm-up / policy window | May reply Stratum 2 per Web serve policy (factory default: lock-based serve) |
| NTP performance | Overload protect ≤ 2048 req/s; design reply capacity ≈ 1500** req/s (V-N10, 16 sources); sustainable (R)** from same report (do not copy 10 k-class appliances) |
| Planning cap | 60 (sales/SNMP; ≠ sync density) |
| Client count | (N (60,R/f_{})), () 0.5–0.7; customer computes from poll rate |
| Per source IP | ≤ 8 replies/s |
| Global replies | Adaptive rate limit; further derated during large Web exports |
| ACL | Optional NTP source IP allow-list (Web) |

Not included: IRIG-B, OCXO, PTP/IEEE 1588 stack (no third-party PTP license pack), NTS, dual-port failover, IPv6, NTP broadcast/multicast server, HTTPS, SNMPv3 / SNMP write. Oscillator class is -T- (TCXO).

## 6. RS-485 Modbus RTU

| Item | Specification |
| --- | --- |
| Link | 9600 8N1 |
| Slave ID | 0x01 |
| Function codes | Read 0x03 / 0x04 (write only for factory use; see protocol annex) |
| Clock registers | UTC Y/M/D/h/m/s/ms |
| Poll rate | Recommend ≥ 1 Hz |

Full register map: Industrial Interface Protocol annex.

## 7. 1PPS & PULSE (summary)

| Item | 1PPS OUT | PULSE (4-pin Pin4) |
| --- | --- | --- |
| Drive | Hardware-buffered 3.3 V TTL | Level-shifted 5 V TTL |
| Role | Metrology second edge | UTC minute PPM (default 200 ms, LOCK only) |
| Absolute time | Pulse = GNSS second boundary | Minute boundary; calendar via Modbus/NTP |
| Not | not a software square-wave on this jack | Impersonating 1PPS; IRIG |
| Accept | Scope on 1PPS jack (1PPS 输出座) | Scope Pin4: ~200 ms at UTC minute after LOCK; mute if unlocked |

## 8. Management & Logs

| Item | Specification |
| --- | --- |
| Web | Dashboard / Network; Basic Auth |
| SNMP | Read-only SNMPv2c, UDP 161; MIB-II system + device status; no Set / SNMPv3 / Trap; enterprise OID per shipping note |
| Syslog | Optional UDP edge push (default OFF); same dictionary as event_log; Web Network configures target IP:514 |
| Event log | event_log.csv (/flog), ring ~2048 entries; default export ~latest 1024; Dashboard → Diagnostics → Export |
| 24 h quality | quality_24h.csv (/stats24); hourly buckets; samples=0 = no GNSS-disciplined samples that hour |
| Front panel | Four pages: patrol / decide / diagnose / asset |

## 9. Ordering & Traceability

Record on the shipping sheet:

Model: TempoSync-3000-BG-T-S
SETID: _______________
Firmware / Build: _______________
Production test: PASS / FAIL

## 10. Related Documents

| Document | Content |
| --- | --- |
| Reference · Serve Policy · Capacity (One Page) | Selection Sheet (Reference · Policy · Capacity) |
| User Guide | Power-up, LCD, Web, clients, FAQ |
| Industrial Interface Protocol | Modbus map, PULSE PPM, 1PPS (hardware fan-out), integration checklist |
| This specification | Contract / selection boundaries |

This document is a shipping/contract summary. Implementation details follow the annex and the shipped firmware.