# Industrial NTP Time Server — Selection Sheet (Reference · Policy · Capacity)

| Item | Content |
| --- | --- |
| Audience | Agents / end customers / tender package |
| Document title | Selection Sheet (Reference · Policy · Capacity) |
| Doc No. | `DOC-Q3000-SEL-EN-011` |
| Model | QYTS-3000-BG-T-S |
| Document version | 1.0 |
| Firmware | V4.9.0-b139+ (see device Web / label) |
| Use | Selection / bid / acceptance (status — policy — capacity one-pager) |
| Companion | Shipping Product Specification Product Specification (Shipping) in this folder |

# 1. Reference source status

Time reference = GNSS 1PPS + disciplined local clock (not PTP; not dual-clock failover).

| Device state (Web / LCD) | Meaning | NTP under factory policy |
| --- | --- | --- |
| LINK up | Ethernet link OK | NTP / Web possible |
| GNSS fix / satellites | Module positioning valid | Discipline in progress |
| Warm-up (synced + PPS, not yet LOCK) | Cold-start converge | May reply Stratum 2 |
| LOCK | Reference ready | Stratum 1 |
| Brief PPS loss (after LOCK) | PPS blip window (~≤10 s) | May still reply |
| Unlock / holdover | GNSS or discipline lost | See §2 |
| No LINK | Cable / switch fault | No NTP |

Do not mix layers: internal/1PPS are hardware-edge metrics; Ethernet NTP is typically millisecond-class on LAN (measure at the client); Modbus resolution 1 ms.

# 2. NTP serve policy (Web)

| Web name | LCD `Pol` | Warm-up | After LOCK | After GNSS unlock |
| --- | --- | --- | --- | --- |
| Lock-based (factory default) | `LCK` | May S2 | S1 | Stop (except brief PPS blip) |
| Lock + timed hold | `TIM` | Same | S1 | Still S2 for ~≤5 min (preferred for Web export / soak) |
| Holdover serve | `HLD` | Sync → reply, usually S2 | Usually S2 | Continues (legacy “always need packets”) |

Saved on Network page; persists across reboot.

Prefer Lock + timed hold during large Web CSV/HTML exports.

Optional NTP ACL is independent of the table above.

# 3. Capacity boundaries (contract numbers)

| Boundary | Spec | Note |
| --- | --- | --- |
| Recommended clients | ≤ 60 on LAN | Default commitment; slow poll typical |
| Per-source IP | ≤ 8 replies/s | Anti-abuse |
| Global overload protect | ≈ ≤ 1024 replies/s | Adaptive: no low hard cap in normal load |
| During large Web export | Global cap further derated | Shared single port with NTP |
| Not included | PTP, dual-port failover, IPv6, NTP broadcast/multicast, NTS, HTTPS, SNMPv3 | Entry industrial NTP; on-device SNMP is v2c read-only only |

Acceptance: After LOCK, LAN `w32tm` / `sntp` OK; Web NTP Served increases; do not accept “module ns” as “client ns”.

# 4. Quick answers

| Question | Answer |
| --- | --- |
| When is official Stratum 1? | LOCK under lock-class policy |
| Cold start with no time for clients? | Default allows warm-up S2; use timed hold for unlock behavior |
| How many clients? | ≤60 recommended — not a 10k+ req/s appliance |
| Meinberg peer class? | Entry industrial NTP (M150/M250-class use) — not IMS / PTP / SyncFire |

Filename Selection Sheet. Interfaces: Industrial IF Protocol; operations: User Guide. Firmware as shown on device.